Effect of Heat Pump Commissioning Faults on Energy Use in a Slab-on-Grade Residential House

Piotr A. Domanski(a),, Hugh Henderson(b), W. Vance Payne(a)

(a) National Institute of Standards and Technology, Gaithersburg, MD 20899-8631, USA

(b) CDH Energy Corporation, Cazenovia, NY 13035-0641, USA

ABSTRACT

This study seeks to develop an understanding of the effect of commissioning common faults on the energy consumption of an air-to-air heat pump installed in a single-family, slab-on-grade residential house.  Through annual simulations of the house/heat pump system, the study found that duct leakage, refrigerant undercharge, oversized heat pump with nominal ductwork, low indoor airflow due to undersized ductwork, and refrigerant overcharge have the most potential for causing significant performance degradation and increased annual energy consumption. Depending on the faults involved, the effects of simultaneous faults were found to be additive, little changed relative to the single fault condition, or well-beyond additive.  A significant increase in annual energy use can be caused by lowering the thermostat setting in the cooling mode to improve indoor comfort in cases of excessive indoor humidity levels due to installation faults.

Keywords: air conditioner, commissioning, energy efficiency, heat pump, space conditioning

- Introduction

Space cooling is responsible for the largest share (21.3 %) of the electrical energy consumption in the U.S. residential sector [1]. Space heating, for which a significant portion is provided by heat pumps, accounts for an additional 8.7 % electricity use. Consequently, there are increasing requirements that space-conditioning equipment be highly efficient to improve building energy efficiency as well as address environmental concerns. To this end, state and municipal governments and utility partners have implemented various initiatives that promote sales of high-efficiency air conditioners and heat pumps.  However, there is a growing recognition that merely increasing equipment’s laboratory-measured efficiency without ensuring that the equipment is installed and operated correctly in the field is ineffective.

This paper discusses the effect of different commissioning faults on heat pump performance for a single-family, residential, slab-on-grade house. The results presented here were derived from a comprehensive and detailed study by Domanski et al. [2].

- Installation and maintenance issues

Numerous field studies have documented degraded performance and increased energy usage for typical air conditioners and heat pumps installed in the United States. For example, Proctor [3] performed measurements on a sample of 28 air conditioners newly installed in 22 residential homes in a hot-and-dry climate.  Indoor heat exchanger airflow averaged 14 % below specifications, and only 18 % of the systems had a correct amount of refrigerant. The supply duct leakage averaged 9 % of the air handler airflow, and the return leakage amounted to 5 %.  Rossi [4] presented measured performance data on unitary air conditioners based on observations from routine maintenance and service visits. Out of 1468 systems considered in this study, 67 % needed service. Of those 15 % required major repairs (e.g., compressor or expansion device replacement), and 85 % required a tune-up type service (e.g., coil cleaning or refrigerant charge adjustment).  Approximately 50 % of all units operated with efficiencies of 80 % or less, and 20 % of all units had efficiencies of 70 % or less of their design efficiency. Among others, Parker et al. [5] and Mowris et al. [6] also provided data on performance degradation of air conditioners and heat pumps due to different faults.

- Technical approach of the study

  - Scope

To evaluate the effect of different commissioning faults on energy consumption, we performed annual simulations of energy use by an air-to-air heat pump installed in a slab-on-grade house. We used the annual energy use in a fault-free installation as a reference for normalizing energy use in faulty installations and for indicating the impact of specific faults on energy consumption. The parameters considered in the simulations included duct leakage (unconditioned space), heat pump sizing, indoor coil airflow, refrigerant charge, presence of non-condensable gases, electrical voltage, cooling-mode TXV undersizing, and five US climate zones 2 through 6 from a hot-and-humid climate to a cold climate, represented by five cities (Table 1).  We used a building model developed in TRNSYS to simulate the integrated performance of heat pumps in residential applications [7].  The model is driven by typical meteorological year weather data sets TMY3 [8] on a small time-step (e.g., 1.2 minutes).  A detailed thermostat model turns the mechanical systems "on" and "off" at the end of each time step depending on the calculated space conditions.

Table 1. IECC US climates and locations considered with thermostat set points and electricity cost

| Zone | Climate | Location | Thermostat set point (°C) |  | Electricity cost |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Cooling | Heating | $/MJ | $/kWh |
| 2 | Hot and humid | Houston, TX | 25.6 | 22.2 | 0.306 | 0.085 |
| 3 | Hot and dry climate | Las Vegas, NV |  |  | 0.454 | 0.126 |
| 4 | Mixed climate | Washington, DC | 24.4 | 21.1 | 0.508 | 0.141 |
| 5 | Heating dominated | Chicago, IL |  |  | 0.461 | 0.128 |
| 6 | Cold | Minneapolis, MN |  |  | 0.389 | 0.108 |

Note:  Electric costs from Form 826 data for local utility in 2010 for residential sector [9]

  - Building specifications

The simulated residential building corresponded to a code-compliant house with a Home Energy Rating System (HERS) score of approximately 100 [10] with appropriate levels of insulation and other features corresponding to each climate.   It was a 185.8 m2 three-bedroom structure with a separate attic zone, which was not conditioned (Figure 1).  It had perimeter slab insulation in climate zones 4 and 5.  A ‘fictitious layer’ was added into the resistance between the zone and ground temperature. This fictitious R-value was used to provide the amount of heat loss through the surfaces determined by the F-factor method (Reffective), as recommended by Winkelmann [11].

The above-ground portions of the houses had exterior walls with layers of drywall, insulation (R(SI)-2.3 or R(SI)-3.3, depending on the climate zone), and stucco as the outside surface. Windows took up approximately 22 % of all of the exterior walls; 10.2 m2 on the north and south facing walls, and 6.5 m2 on east and west facing walls. The ceiling (i.e. boundary between main zone and attic) was made up of a layer of drywall, framing and insulation (R(SI)-5.3 or R(SI)-6.7, depending on the climate zone).  The attic had gable walls on the east and west sides and roof surface on the north and south sides. The roof was sheathed in plywood and then covered with asphalt shingles. The east and west surfaces (gables) are made up of plywood on the inside surface with stucco on the outside surface.

The AIM-2 infiltration model [12, 13] relates infiltration to wind and indoor-outdoor temperature difference for each time step. An equivalent leakage area (ELA) of 0.0633 m2 was chosen to provide the desired seven air changes per hour (ACH) at 50 pascal pressure differential (ACH50 for the main zone in each building model).  The attic used the same AIM-2 equations to determine leakage as a function of wind and temperature difference.  The attic ELA was set to be 0.366 m2 for each of the climate zones, or about 5 times the leakage rate for the HERS 100 house [14].

24.5 mm carpet

Tground

0.3 m soil

101 mm concrete

Rfic-floor

Supply leak to attic

Return leak from attic

AHU

Figure 1. Schematic of a slab-on-grade house (ducts located in the unconditioned attic)

The ducts were modeled to be in the attic space and all the air leakage and thermal losses/gains go into that zone. Duct leakage was assumed to be 10 % of flow; 6 % on the supply side and 4 % on the return side.  Duct insulation was assumed to be R(SI)-1.1 with a supply duct area of 50.5 m2 and a return duct area of 9.3 m2 for a 10.6 kW.  The nominal duct areas were increased and decreased proportionally based on the size (or nominal tonnage) of the heat pump unit.

The window model in Type 56 uses the window parameters generated by LBNLs WINDOW5 software, which is considerably more detailed than the NFRC rating values generally used in residential practice and building codes.  The LBNL WINDOW5 inputs for this project were determined following the methodology developed by Arasteh et al. [15].

The scheduling or profile of internal heat and moisture generation was taken from the Building America Benchmark Definition [16].  Sensible gains from all sources were assumed to be 76.7 MJ/day.  Internal moisture generation from all sources was specified as 5.4 kg/day, or less than half of the ASHRAE Standard 160 moisture generation rate of 14.2 kg/day for a three-bedroom house [17].  The ASHRAE 160 value is meant to be a ‘worst case’ design condition and therefore does not correspond to average conditions.

The only mechanical ventilation option considered in this study is an exhaust fan.  The fan operated continuously to provide sufficient ventilation to the house.  The fans provided an average flow rate of 98.5 m3∙h1 required by ASHRAE Standard 62.2 [18] for the 185.8 m2 three-bedroom house.  The exhaust fan power was assumed to be 0.85 kJ∙m-3.  The duct leakage was always a net out, so that additional net flow was an exhaust.  All detailed house design specifications are given by Domanski et al. [2].

### Heat pump specifications and modeling

Fault effects were measured and correlated for a conventional heat pump unit with a 13 SEER and 7.7 HSPF rating. The cyclic degradation coefficient, CD, of the heat pump was approximately 0.15 in both cooling and heating mode.  For determining the performance of a faulty heat pump, we applied dimensionless multipliers to the fault-free heat pump performance parameters (capacity, COP, etc.) [21, 22]. The reader may refer to Domanski at al. [2] for definitions of the studied faults and for more detail on modeling of a fault-free and faulty heat pump.

The required size of the unit was determined for each climate using ACCA Manual J [19]. Houses in Houston and Las Vegas had a heat pump with cooling capacity of 10.6 kW and 12.3 kW, respectively.  The Washington D.C., Chicago, and Minneapolis houses had 8.8 kW units. We modeled the performance of the simulated fault-free heat pumps using a detailed heat pump model derived from catalog data from a series of single-speed heat pump products with permanent split capacitor blower motors and SEER ratings ranging from 10 to 14.5 [20]. Table 2 lists the studied faults and their level values used in simulations.

Table 2.  Studied faults in the cooling and heating mode

| Fault Type | Fault Levels (%) |  |
| --- | --- | --- |
|  | Cooling mode | Heating mode |
| Heat Pump Sizing (SIZ) | -20, 25, 50, 75, 100 | -20, 25, 50, 75, 100 |
| Duct Leakage (DUCT) | 0, 10, 20, 30, 40, 50 | 0, 10, 20, 30, 40, 50 |
| Indoor Coil Airflow (AF) | -36, -15, 7, 28 | -36, -15, 7, 28 |
| Refrigerant Undercharge (UC) | -10, -20, -30 | -10, -20, -30 |
| Refrigerant Overcharge (OC) | 10, 20, 30 | 10, 20, 30 |
| Non-Condensable Gases (NC) | 10, 20 | 10, 20 |
| Electric Voltage (VOL) | -8, 8, 25 | -8, 8, 25 |
| TXV Undersizing (TXV) | -60, -40, -20 | - |

# Simulations of building/heat pump systems with installation faults

4.1 Simulation with single faults

    - Effect of heat pump sizing

Changing the size of the heat pump for a given house – either undersizing or oversizing – impacts the heat pump performance in several ways:

- Cycling losses increase as the unit gets larger; the unit runs for shorter periods and the degraded performance at startup has more impact (CD ~ 0.15).

- In the cooling mode, the shorter run periods impact the moisture removal capability (i.e., ability to control indoor humidity levels) because operational steady-state conditions are an even smaller portion of the runtime fraction.

- In the cooling mode, continuous fan operation with compressor cycling greatly increases moisture evaporation from the cooling coil. However, this impact is minimal with auto fan control (indoor fan time ‘on’ and ‘off’ the same as that of the compressor), since only a small amount of evaporation occurs with the assumed 4 % airflow during the off-cycle with the indoor fan off.   If the air conditioner controls include an off-cycle fan delay – that keeps the fan on for 30-90 seconds after the compressor stops – then the impact of off-cycle evaporation is in between these two extremes [23].  The results in this study assumed auto fan operation with no fan delay.

- In the heating mode, the backup heater runtime is lower for the oversized unit since the larger heat pump meets more of the winter heating needs.

Heat pump sizing also affects the level of duct losses, and different oversizing scenarios are possible depending on the relative size of the heat pump and ductwork. The scenario considered in this paper represents the case where the ductwork has been sized for a heat pump of nominal capacity and remains unchanged for different size heat pumps. When the heat pump is oversized, the fan speed is increased but the airflow does not reach the target flow rate because the unit is not capable of overcoming the increased external static pressure. Since the indoor fan works against increased static pressure, the fan power changes per the fan curve, i.e., fan power increases with an increasing unit size. The increased pressure in the duct increases the duct leakage.  The increased fan power (while working against increased static pressure) and increased fan heat added to the load are the main factors contributing to the significant increase in energy used in cooling-dominated climates (Houston, Las Vegas, Washington, DC).  These factors are mitigated in heating-dominated climates (Chicago and Minneapolis) since the oversized heat pump reduces the use of the electric resistance backup heat.

Table 3 shows in detail the effect of sizing on the total performance for Houston and Minneapolis to contrast the detailed results obtained for a cooling-dominated climate with those for a heating dominated climate. The threshold 55 % relative humidity value used in the third column was selected as the level above which humidity might start to be a concern.  The ‘Space Temp Max’ column contains the highest indoor temperature reached during the cooling season. The column ‘AC Energy’ contains the energy used by the compressor and outdoor fan to provide cooling; the column ‘Htg Energy’ contains the energy used by the compressor, outdoor fan, and backup heat to provide heating; and the column ‘AHU Fan Energy’ contains the energy used by the indoor fan during the whole year. The column ‘TOTAL ENERGY’ contains the total energy used by the heat pump throughout the entire year, which consists of the energy use listed in the three previous columns, and the energy used by the home exhaust fan.

Table 3. Effect of heat pump sizing on annual energy use for a house with a fixed duct size

At first glance, the reader may be surprised by a decrease in the energy use in houses located in cooling-dominated climates when the heat pump is undersized. The lower energy use is a result of the heat pump unable to handle all the cooling load (the indoor temperature increases on hot days). For the heating dominated climates, the energy use is increased because of the significantly increased use of the resistance heat. Figure 2 shows relative energy input for houses in all locations.

Figure 2. Annual energy use for houses for different heat pump sizings

Another somewhat surprising result is the impact that oversizing has on space humidity levels.  The number of hours exceeding 55 % RH decreases when the unit is oversized, especially in Houston.  This reduction is primarily due to effect of duct leakage:  the larger unit size reduces the fan runtime thereby reducing the amount of moisture brought into the house via return air leaks.  A secondary factor in lowering humidity levels is the increases sensible gains (or heat) provided by the increases fan power for the oversized unit.

    - Effect of duct leakage

The baseline houses include ducts in the attic with a leakage rate of 10 % (leakage distributed 60 % on the supply side and 40 % on the return side) as well as thermal losses through the duct wall.  Table 4 compares this base case to other levels of duct leakage with the thermostat set at the default set point temperature (Table 1).  The entry ‘0 % & No thermal’ in the left most column denotes an idealized installation with zero air leakage and no thermal loss (i.e., an insulation with an infinite R or ducts located in the conditioned space).

As expected, the baseline duct losses increase energy use in the baseline houses; our simulations showed a 20 % and 30 % increase for the cooling climates and heating climates, respectively, compared to the 0 % leak/no thermal loss case.  As the duct leakage increases, energy use increases by at least 8 % for the cooling climates and by 12 % for the heating climates for each 10 % increment in the duct leakage fault. A slight improvement of the cooling COP shown with the increasing fault level is caused by a somewhat higher refrigerant saturation temperature (and pressure) in the evaporator when the air returning to the indoor section is at higher temperature and humidity due to duct losses. This COP improvement, however, can’t compensate for the significant increase in the cooling load, which is the cause of the increased energy use.

Table 4.  Effect of duct leakage on annual energy use at default cooling set point

Note: All simulation cases account for thermal losses along with leakage losses except the case denoted ‘0 % & No thermal’.

Since the number of hours with relative humidity above 55 % increases with duct leakage, a homeowner may be inclined to lower the thermostat cooling set point to improve indoor comfort. Figure 3 presents the relative energy use for a slab-on-grade house in Houston with different duct leak rates at the three studied thermostat set point temperatures. The energy use is related to that of a house with 10 % leak rate (assumed as a representative of no-fault duct installation) at the default thermostat set point. Energy use increases by almost 17 % and 60 % as the thermostat is lowered by 1.1 °C and 2.2 °C, respectively. For the house with a 40 % duct leakage, the energy use is predicted to be 47 % and 97 % higher than for the reference house if the set point temperature is lowered by 1.1 °C and 2.2 °C, respectively.

Figure 3. Energy use for duct leak rates from 10 % to 50 % at the default thermostat set point temperature and two set points lowered by 1.1 °C and 2.2 °C related to energy use for the house at the default set point and 10 % leak rate in Houston

    - Effect of indoor coil airflow

This fault covers the case where a heat pump properly sized for the building load operates with improperly sized ductwork. As a result, the indoor coil airflow is not nominal. The simulated indoor airflows, ranging from -36 % to +28 % of the designed air flow, corresponded to external static pressures of (177, 171, 168, 165, and 149) Pa, respectively. Reduced airflow results in an increase in energy consumption, and this effect is similar for all houses in all climates studied (Figure 4).  For the lowest airflow, 36 % below the nominal value, the energy use increased from 11 % to 14 %.

Figure 4. Annual energy use for houses with different indoor coil airflows relative to energy use for the house in the same location with nominal airflow rate

In the cooling mode, reducing the capacity specific airflow below the nominal value of 181.1 m3∙h-1∙kW-1  causes a decrease in the indoor coil temperature and provides better humidity control, but results in higher energy use because the sensible capacity is reduced and running time increased. Conversely, providing more airflow hurts humidity control in the house but decreases energy use.  The efficiency of the system goes up, and more importantly, the latent removal decreases so energy use decreases.

    - Effect of refrigerant undercharge

When the amount of refrigerant charge in the TXV-controlled system is below the nominal value, the performance of the unit is degraded (Figure 5).  The figure indicates that the energy use increases exponentially with increasing refrigerant undercharge. For the 30 % refrigerant undercharge level the energy use increases by as much as (17 ~ 23) %. The moisture removal capacity of the unit is also degraded when the unit is undercharged.

Figure 5.  Annual energy use at different levels of refrigerant undercharge relative to the annual energy use for the house in the same location when the heat pump operates with the nominal refrigerant charge

4.1.5. Effect of refrigerant overcharge

When the amount of refrigerant charge in the system is above the correct (nominal) value, the performance of the unit is degraded (Figure 6).  The heat pump uses (10 ~ 16) % more energy when overcharged by 30 %, with somewhat higher increases in energy use occurring in localities with a significant heating season (i.e., Chicago, Washington DC, and Minneapolis). The moisture removal capability of the unit is not affected by the overcharge fault.

Figure 6. Annual energy use at different levels of refrigerant overcharge relative to the annual energy use for the house in the same location when the heat pump operates with the nominal refrigerant charge

4.1.6 Effect of non-condensable gases

If the refrigerant system has non-condensable gases (e.g., air) mixed in with the refrigerant, the performance of the unit is degraded. The overall simulation results showed a (1 ~ 2) % energy use increase in climates with a significant heating season and a 4 % increase in the warmer climates. The moisture removal capability of the unit is only minimally affected by the non-condensable gases in the system.

    - Effect of voltage

When input voltage to the unit is changed from the nominal value, the performance of the unit is degraded. The condition of 25 % overvoltage results in a (9 ~10) % increase in annual energy consumption. This effect on the energy use does not include an adjustment for indoor fan power change with voltage.  The undervoltage of 8 % resulted in an insignificant (within 1 %) change in the energy use. Higher levels of undervoltage were not studied because of a possible heat pump catastrophic failure.

4.1.8. Effect of TXV sizing

Undersizing of the TXV only in the cooling mode is considered in this study.  When the size of the TXV does not match the compressor size, the performance of the system is degraded (Figure 7).  Generally, the impact is modest at 20 % undersizing in any climate and remains relatively small for Minneapolis at even higher fault levels. However, the impact becomes significant at 40 % undersizing, particularly in hot climates where the energy use increases by (10 ~ 14) %.  Moisture removal is only modestly affected.

Figure 7. Annual energy use for slab-on-grade houses at different levels of TXV undersizing relative  to the annual energy use for the house when the heat pump operates with a properly sized TXV

4.1.9 Discussion of the effects of single faults

Figure 8 shows examples of annual energy used by a heat pump installed with different installation faults in a slab-on-grade house.  The levels of individual faults were selected to reflect, to some degree, the installation condition which might not be noticed by a poorly trained technician (Table 5).  (The authors recognize the speculative aspect of this selection.)

Figure 8. Annual energy use resulting from a single-fault installation, referenced to a fault-free installation. (Table 5 shows the selected fault levels)

Table 5. Levels of individual faults used in Figure 8

| Fault Type | Fault Level (%) |
| --- | --- |
| Heat Pump Sizing (SIZ) | + 50 |
| Duct Leakage (DUCT) | 30 |
| Indoor Coil Airflow (AF) | - 36 |
| Refrigerant Undercharge (UC) | - 30 |
| Refrigerant Overcharge (OC) | + 30 |
| Non-Condensable Gases (NC) | 10 |
| Electric Voltage (VOL) | + 8 |
| TXV Undersizing (TXV) | - 40 |

The duct leakage fault has the potential to result in a higher increase in energy use than any other fault. The impact of this fault is higher for the heating dominated climate (Chicago and Minneapolis, 26 %) than for the cooling dominated climate (Houston, 18 %). The second most influential fault is refrigerant undercharge. For the 30 % undercharge fault level, the energy use increase is of the order of 20 % irrespective of the climate and building type. Refrigerant overcharge can also result in a significant increase in energy use, (10 ~16) % at the 30 % overcharge fault level. Improper indoor airflow can affect similar performance degradation.

Installation of an oversized heat pump resulting in an over-restrictive ductwork leads to a significant increase in energy use; 15 % increase in energy use was predicted for the house in Houston.  The cooling TXV undersized fault also has the potential to significantly increase the energy use. The effect of this fault will be most pronounced in localities with a high number of cooling mode operating hours. The cooling mode TXV undersized by 40 % results in (9 ~ 14) % more energy used in Houston as compared to a (3 ~ 5) % more in Chicago.  The impact of the remaining faults – non-condensables and improper voltage – is under 4 %.  The non-condensables and improper voltage faults, however, represent a substantial risk for durability of equipment and are very important to be diagnosed during the heat pump installation.

4.2 Simulations with dual faults

4.2.1. Studied fault combinations

Table 6 lists combinations of the two simultaneous faults studied, A and B.  Each set of faults was considered in four combinations (Table 7).  The moderate level was the value at the middle of the range, while the worst level was the highest (or lowest) probable level of the fault value.  Simulations were performed for 14 dual fault sets, with 4 runs per set, in 5 house/climate combinations for a total of 280 runs.

Table 6. Dual fault sets considered in simulations of annual energy use and their approximate collective effect on annual energy use

| Fault set # | Fault A levels (moderate & worst level)(a) (%) | Fault B levels (moderate & worst level) (%) | Effect on energy use |
| --- | --- | --- | --- |
| 1 | Duct leakage (20, 40) | Oversize (25, 50) | A+B |
| 2 | Duct leakage (20, 40 ) | Indoor coil airflow (-15, -36) | < A+B |
| 3 | Duct leakage (20, 40) | Refrigerant undercharge (-15, -30) | A+B or > A+B |
| 4 | Duct leakage (20, 40) | Refrigerant overcharge (15, 30) | A+B |
| 5 | Duct leakage (20, 40 ) | Non-condensables (10 , 20 ) | A+B |
| 6 | Oversize (25, 50) | Refrigerant undercharge (-15, -30) | A+B |
| 7 | Oversize (25, 50) | Refrigerant overcharge (15, 30) | A+B |
| 8 | Oversize (25, 50) | Non-condensables (10, 20) | A+B |
| 9 | Indoor coil airflow (-15, -36) | Refrigerant undercharge (-15, -30) | < A+B |
| 10 | Indoor coil airflow (-15, -36) | Refrigerant overcharge (15, 30) | < A+B |
| 11 | Indoor coil airflow (-15, -36) | Non-condensables (10, 20) | < A+B |
| 12 | Duct leakage (20, 40) | Cooling TXV undersizing(b) (-20, -60) | A+B |
| 13 | Oversize (25, 50) | Cooling TXV undersizing(b) (-20, -60) | A+B |
| 14 | Indoor coil airflow (-15, -36) | Cooling TXV undersizing(b) (-20, -60) | < A+B |

(a) moderate = mid-level value,    worst = lowest/highest level value

(b) Fault exists only in the cooling mode; the heating mode TXV is sized correctly

Table 7.  Combinations of studied faults

| Fault combination case | Level of fault A | Level of fault B |
| --- | --- | --- |
| a | moderate | moderate |
| b | moderate | worst |
| c | worst | moderate |
| d | worst | worst |

4.2.2. Effects of dual faults

The most right-hand column in Table 6 shows an approximate effect of the studied fault sets on the energy use: the faults effects may be additive (A+B), less than additive (<A+B), or greater than additive (>A+B). As expected, the collective impact of two simultaneous faults on the energy consumption varies and depends on the faults considered. In most cases (9 out of 14 fault sets), the collective effect can be described as being additive; however, for the remaining five sets – all involving indoor coil airflow –  the effect can be markedly below this additive value, including being approximately equal to the individual effect of one of the faults involved. The above characterization applies to all house/climate combinations. Figure 9 presents annual energy use for all studied dual fault sets at the five locations for the worse fault levels. The figure shows the most severe performance degradation with dual faults involving duct leakage.

Figure 9. Annual energy use with 14 dual faults relative to the energy use for fault-free installation (Faults defined in Tables 6; Table 7 case d, the worst level for both faults)

5. Concluding remarks

Extensive simulations of house/heat pump systems in five climatic zones lead to the following conclusions:

- Duct leakage, refrigerant undercharge, oversized heat pump with non-oversized ductwork, low indoor airflow due to undersized ductwork, and refrigerant overcharge have the most potential for causing significant performance degradation and increased annual energy consumption. Increases of energy use by 30 % due to improper installation practices seem to be plausible.

- Effects of different  installation faults are similar in different climates except for the following cases:

- Duct leakage causes a significant increase in the indoor RH for installations in a hot & humid

climate

- Heat pump oversizing with undersized air ducts causes stronger performance degradation in

cooling-dominated climates than in in heating-dominated climates, where the increased

indoor fan energy use associated with the overcoming of the higher external static pressure is

compensated by the reduced use of backup resistance heat

- Undersized cooling-mode TXV has little effect in heating-dominated climates, while a significant increase of energy use is possible in cooling-dominated climates.

- The effect of simultaneous faults can be additive (e.g., duct leakage and non-condensable gases), little changed relative to the single fault condition (e.g., low indoor airflow and refrigerant undercharge), or well-beyond additive (duct leakage and refrigerant undercharge).

- A significant increase in annual energy use can be caused by lowering the thermostat in the cooling mode to improve indoor comfort in cases of excessive indoor humidity levels.

The goal of this study was to assess the impacts that HVAC system installation faults had on equipment electricity consumption.  The effect of the installation faults on occupant comfort was not the main focus of the study, and this research did not seek to quantify any impacts on indoor air quality, or noise generation (e.g., airflow noise from air moving through restricted ducts).  Additionally, the study does not address the effects that installation faults have on equipment reliability/robustness (number of starts/stops, etc.), maintainability (e.g., access issues), or costs of initial installation and ongoing maintenance.

References

[1]  DOE, 2011 Buildings Energy Data Book, Residential Sector Energy Consumption. U.S. Department

of Energy. Retrieved online at http://buildingsdatabook.eren.doe.gov/docs/xls_pdf/2.1.6.pdf,

September 30, 2014

[2]  Domanski, P.A., Henderson, H., Payne, W.V., Sensitivity Analysis of Installation Faults on Heat

Pump Performance. NIST Technical Note 1848, National Institute of Standards and Technology,

Gaithersburg, MD., http://dx.doi.org/10.6028/NIST.TN.1848, (2014).

[3]  Proctor, J.P., Field Measurements of New Residential Air Conditioners in Phoenix, Arizona. ASHRAE

Transactions, 103(2), 406-415. http://www.ashrae.org, (1997).

[4]  Rossi, T.M., Unitary Air Conditioner Field Performance. International Refrigeration and Air

Conditioning Conference at Purdue, Paper No. R146, West Lafayette, IN., (2004).

[5] Parker, D.S., P.A. Broman, J.B. Grant, L. Gu, M.T. Anello, R.K. Vieira, H.I. Henderson. 1999.

ENERGYGAUGE USA: A Residential Building Energy Simulation Design Tool. Proceedings of Building Simulation '99, Volume 1 (1999) 73-79.

[6] Mowris, R.J., Blankenship, A., Jones, E., 2004. Field Measurements of Air Conditioners with and

without TXVs. ACEEE 2004 Summer study on Energy Efficiency in Buildings, American Council for an Energy Efficient Economy, Washington, DC. http://www.aceee.org, (2004).

[7] 	CDH Energy Corp.,  TRN-RESDH5:  TRNSYS Residential AC/Dehumidifier Model – SHORT

TIMESTEP.  A Tool for Evaluating Hybrid Configurations and Control Options in Single-Zone Building Applications, Operating and Reference Manual. Cazenovia, NY., (2010).

[8]  Wilcox, S., Marion, W., Users Manual for TMY3 Data Sets, Technical Report

NREL/TP-581-43156, http://www.nrel.gov/docs/fy08osti/43156.Pdf, (2008).

[9] EIA, Form 826 data for local utility in 2010 for residential sector. U.S. Energy Information

Agency,  http://www.eia.gov/cneaf/electricity/page/eia826.html, (2012).

[10] RESNET, 2006. Home Energy Rating System (HERS), Residential Energy Services Network 	http://www.resnet.us/, (2006).

[11] Winkelmann, F., Underground Surfaces: How to Get a Better Underground Surface Heat Transfer

Calculation in DOE-2.1E.  Building Energy Simulation User News, Vol. 19, No. 1, (1998).

[12] Walker, I., Wilson, D. Field Validation of Algebraic Equations for Stack and Wind Driven Air

Infiltration Calculations. International Journal of HVAC&R Research (now ASHRAE HVAC&R Research Journal), 4(2). http://aceee.org, (1998).

[13] ASHRAE, ASHRAE Handbook of Fundamentals.  Chapter 17, Residential Cooling and Heating Load

Calculations.  American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Atlanta, GA. http://www.ashrae.org, (2009).

[14] Fugler, D., Conclusions from Ten Years of Canadian Attic Research.  ASHRAE Transactions, 105(1).

http://www.ashrae.org, (1999).

[15] Arasteh, D., C. Kohler, B. Griffith, Modeling Windows in Energy Plus with Simple Performance

Indices.http://windows.lbl.gov/win_prop/ModelingWindowsInEnergyPlusWithSimplePerformanceIndices.pdf, (2009)

[16] Hendron, R., Building America Research Benchmark Definition. Technical Report, NREL/TP-550-

44816, Updated December 19, 2008, National Renewable Energy Laboratory, Golden, CO., (2008).

[17] ASHRAE, ANSI/ASHRAE Standard 160-2009, Criteria for Moisture-Control Design Analysis in

Buildings, American Society of Heating. Refrigerating, and Air-Conditioning Engineers, Atlanta, GA. http://www.ashrae.org, (2009).

[18] ASHRAE, ANSI/ASHRAE Standard 62.2, Ventilation and Acceptable Indoor Air Quality in

Low-Rise Residential Buildings. American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Atlanta, GA.  http://www.ashrae.org, (2013)

[19] ACCA, ANSI/ACCA 2 Manual J – 2011, Residential Load Calculation 8th Edition. Air Conditioning

Contractors of America, Arlington, VA., http://www.acca.org/

[20] Parker, D.S., Sherwin, J.R., Raustad, R.A., Shirey, D.B. III. Impact of Evaporator Coil Airflow in

Residential Air-Conditioning Systems. ASHRAE Transactions, 103(2), 395-405. http://www.ashrae.org, (1997).

# [21]	Kim, M., Payne, W. V., Domanski, P. A., Yoon, S. H., Hermes, C.J.L., Performance of a Residential

# Heat Pump Operating in the Cooling Mode with Single Faults Imposed. Applied Thermal

# Engineering 29(4), 770-778, (2009)

# http://dx.doi.org/10.1016/j.applthermaleng.2008.04.009, (2009).

[22] Cho, J.M., Payne, W.V. Payne, Domanski, P.A., Normalized Performance Parameters for a

Residential Heat Pump in the Cooling Mode with Single Faults Imposed, Applied Thermal Engineering, 67(1-2), 1-15, http://dx.doi.org/10.1016/j.applthermaleng.2014.03.010, (2014).

[23] Shirey, D.B., Henderson, H.I.,  Raustad, R., 2006. Understanding the Dehumidification Performance

of Air-Conditioning Equipment at Part-Load Conditions. Final Report FSEC-CR-1537-0. DOE/NETL Project No. DE-FC26-01NT41253. Florida Solar Energy Center, Cocoa, FL. http://www.fsec.ucf.edu/en

Acknowledgement

This study was performed within Annex 36, Quality Installation/Quality Maintenance Sensitivity Study Analysis, of the International Energy Agency Heat Pump Program. The authors acknowledge Van Baxter of the Oak Ridge National Laboratory, Oak Ridge, TN, and Glenn Hourahan of the Air Conditioning Contractors of America, Arlington, VA, for organizing and managing the Annex.  The authors also thank Glenn Hourahan for suggesting the scope of this study and for sharing his practical insights during different phases of the project, and Brian Dougherty of NIST for his expert review of the manuscript.

Nomenclature

ACH50			= air changes per hour at 50 pascal pressure differential

AF 		= improper indoor airflow rate fault

AHU			= air handling unit

CD			= heat pump cyclic degradation coefficient

COP 		= coefficient of performance

DUCT		= duct leakage fault

ELA			= equivalent leakage area [m2]

HSPF			= heating seasonal performance factor

HVAC			= heating, ventilating, air conditioning

Htg			= heating

NC			= presence of non-condensable gases fault

OC	= refrigerant overcharge fault, % (or fraction) departure from the correct value

R(SI)				= thermal resistance in SI system of units [K∙m2∙W-1]

RH				= relative humidity [%]

SEER				= seasonal energy efficiency ratio [(Btu∙W-1∙h-1)]

SIZ	= heat pump sizing fault, % (or fraction) above or below the correct capacity

T 	= temperature [C]

TMY3	= data set 3 with typical meteorological year weather data

TXV	= thermostatic expansion valve or TXV undersizing fault in cooling

UC	= refrigerant undercharge fault, % (or fraction) departure from the correct value

VOL 	= electric line voltage fault

Corresponding author; piotr.domanski@nist.gov; tel: 301-975-5877